## Slide 1: RO Diagnostics- Anomaly Detection Model

## Slide 2: Data Collection
DATA Collection:
Raw data was sourced from ETP-RO plant manual field records and laboratory analysis, rather than automated sensors.
Since the dataset relies on manual measurements, there may be limitations in terms of data accuracy, consistency, and repeatability.
This process was nonetheless valuable for understanding the full model-building workflow and the steps involved in data analysis and pipeline construction

## Slide 3: Data Loading and Cleaning
Step 1: Data Loading and Cleaning
The raw data from an Excel file was loaded and inspected for structure and missingness, with 643 rows and 38 columns representing various feed, permeate, and reject water quality/operation metrics.
We handled non-detects ("ND"), NA values, and placeholders by converting them to NaN, enabling more robust Pandas handling.
Linear interpolation and forward-filling were used to fill missing values, providing continuity for subsequent analysis. Cleaned datasets were saved at each key cleaning step.

## Slide 4: KPI Calculation
Step 2: Key Performance Indicator (KPI) Calculation
The following KPIs were computed:
  Recovery: Permeate Flow÷Feed Flow×100Permeate Flow÷Feed Flow×100.
  Salt Passage: Permeate TDS÷Feed TDS×100Permeate TDS÷Feed TDS×100.
  Salt Rejection: 100−Salt Passage100−Salt Passage
  Delta P (Pressure Drop): Feed Pressure−Reject Pressure
  Temperature Correction Factor (TCF) and Normalized Permeate Flow (NPF), conditional on the availability of a temperature column.

## Slide 5: Rule Based Diagnostics
Step 3: Key Performance Indicator (KPI) Calculation
The following KPIs were computed:
  Recovery: Permeate Flow÷Feed Flow×100Permeate Flow÷Feed Flow×100.
  Salt Passage: Permeate TDS÷Feed TDS×100Permeate TDS÷Feed TDS×100.
  Salt Rejection: 100−Salt Passage100−Salt Passage
  Delta P (Pressure Drop): Feed Pressure−Reject Pressure
  Temperature Correction Factor (TCF) and Normalized Permeate Flow (NPF), conditional on the availability of a temperature column.

## Slide 6: Forecasting Models
Step 4: Forecasting Models
Permeate Flow Forecast:
  Initial RandomForest regression used only three input features (TDS, feed pressure, reject pressure).
  Model R² was 0.0 (no variance explained) and MAE (mean absolute error) was very low, indicating the permeate flow in the dataset was almost constant.
  Insight: Flow prediction failed because the plant and dataset did not show significant changes in permeate flow values.
  Feature Engineering:
  We extended the feature set for flow prediction (including Recovery, Normalized Salt Passage, TCF), but as the output variable remained flat, model did not improve.

## Slide 7: Forecasting Models
B) Salt Rejection Forecast:
  Model achieved R² = 0.59, meaning about 60% of the variance in rejection could be explained by the input features.
  MAE was also low, and rejection was responsive to feed TDS and operation conditions, so model performed reasonably well for this parameter.

## Slide 8: Forecasting Models
Results Interpretation
Permeate Flow: Consistent, flat operation is good for plant performance, but it limits the predictive capacity of ML models (no variance = no learnable pattern). Also May be wrong the data itself as its not the sensor data.
Salt Rejection: More responsive to changes, thus more predictable with current plant data.
Suggested Next Steps: For meaningful forecasting, future models should:
  Include more influencing features (e.g., temperature, hours in operation, SDI, cleaning etc.).
  Collect datasets reflecting events (fouling, CIP, operational changes), not just stable periods.
  Use sensor data for improved variability and granularity.